## Hot Work Permit Policy

In accordance with the requirements of the Fire Code for the State of New York Fire Chapter 26 and OSHA 29 CFR 1910.252 a Hot Work Permit is required for the following activities: brazing, cutting, heating, soldering, welding or similar type work. The intent of this program is to prevent injury and loss of property from fire when using heat producing equipment such as heat guns, soldering tools, oxy-fuel gas and electric arc cutting and welding equipment.

Hot Work shall be permitted in approved areas and will be issued to both Farmingdale State personnel and outside contractors by Farmingdale State Physical Plant. On occasion, with the approval of Physical Plant, a blanket permit can be granted for a long duration project.

Permit:  In order to obtain the necessary Hot Work Permit, the following shall be ensured;

- The area shall be inspected by Farmingdale State Physical Plant or it’s representative.

- The type of hot work must be approved for the project being performed

- Containers and/or pipes must be properly cleaned, purged and inspected.

- All combustible and flammable material shall be protected/relocated away from the Hot Work area

- Floor and wall openings (within 35’) shall be covered or sealed to prevent fire spread

- Fire detection and suppression equipment must remain operational at all times, unless otherwise protected or approved by Physical Plant and University Police.

- Fire extinguishers of proper size and type shall be located within 25’ of the Hot Work area

- Hot Work equipment such as gas cylinders, hoses, leads and torches shall be properly maintained, secured, stored, transported and used at all times

- Proper personal protective equipment (i.e. clothing, face shields, goggles, gloves, head and foot protection) shall be worn, as required.

- Health and safety hazards such as asbestos, chemical/cleaner usage, confined space, electrical, fire, heat, respiratory, ventilation and other similar issues should be evaluated prior to Hot Work

- A fire watch (not less than ½ hour) shall be performed for each Hot Work Permit issued.

- Bags for smoke detectors shall be supplied and installed by the contractor when necessary

- Permanent or portable curtains and screens must be used if persons are or could be exposed to the direct or reflected radiation

- Exhaust ventilation has been  provided or has been determined to be sufficient

Fire Watcher(s): Farmingdale State may require a separate person to perform a fire watch.

- The fire watcher shall have the proper size and type (fully charged) fire extinguisher within 25’

- The fire watcher shall be properly trained in the proper use and limitations of the fire extinguisher

- The fire watcher shall be familiar with the proper procedures for activating the fire alarm and notification of Farmingdale State University Police.

- The fire watch shall be maintained for at least 1 hour after the Hot Work has been completed

  - ½ hour if approved by Physical Plant.

Gas Storage and Transportation:

- All cylinders must be secured at all times by either an approved chain or strap

- All cylinders must have either a cap or regulator in place at all times

- All cylinders must be stored, transported and used in an upright position

- All cylinders and attached equipment must be free of damage and leaks

- All cylinders must be properly labeled

For more information, contact Mark Orlich, Farmingdale State Physical Plant at 631-420-2215